## NPSH calc
Calculation sheet NPSHr
version 1.0 - 19-01-2015
Customer:
Project:
Engineer:
Date:
Required information
name | value | unit | explanation
Patm. | 9.81 | mwc | Atmospheric pressure
Pressure pressent at the location
(standard at sealevel 9,81 mwc)
Hlosses. | 1.5 | mwc | Pressure losses
Total of in suction pipe, elbows and valves
Hstatic. | -3 | mwc | Static hight
Total hight in mtrs from water level to pump inlet connection
(negative when waterlevel is beneth the pump)
tliquid | 30 | 0C | Water temperature
Actual water temparature to be pumped
NPSHreq. | 2 | m | Required NPSH
Pump required NPSH
(read from the pumpcurve at required capacity)
Calculated results
name | value | unit | explanation
Pvap. | 0.43154 | mwc | Vaporisation pressure
Minimum pressure in suction line to avoid boiling
NPSHavail. | 4.8785 | m | Available NPSH
NPSH that is available as a result of the chosen setup
Margin | 2.8785 | m | Safety margin
The difference between required and available NPSH.
| 2.4392 |  | negative means that the application is impossible!
Advice: | Yes |  | Recomandation
Some literature mention to use a "NPSH margin" for problem free operation. This margin has a ranking from 1 to 5 (NPSHa / NPSH r = 1-5).Totally empirically in this recomandation a ranking of 1,25 is used
Hstatic +
Hstatic -